
Copyright 2020 by The American Institute of Architects (AIA)

Exclusively published and distributed by Deltek, Inc. for the AIA
SECTION 083343 - OVERHEAD COILING SMOKE CURTAINS
Revise this Section by deleting and inserting text to meet Project-specific requirements.
PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Smoke-protective curtain assemblies for elevator entrances.

1.2 PREINSTALLATION MEETINGS

Retain "Preinstallation Conference" Paragraph below if Work of this Section is extensive or complex enough to justify a conference.

A. Preinstallation Conference: Conduct conference at [Project site] <Insert location>.

If needed, insert list of conference participants not mentioned in Section 013100 "Project Management and Coordination."

1.3 COORDINATION

A. Coordinate smoke curtain assemblies with power, signal, fire-alarm, and smoke-detection systems specified in Division 26 and Division 28.

B. Coordinate elevator smoke-protective curtain assemblies with elevator hoistway door frames specified in Division 14.

C. Coordinate smoke-protective curtain assemblies with ceilings for operational clearances and maintenance access requirements.

D. Coordinate smoke-protective curtain assemblies with walls for support requirements, rating continuity above ceilings, and recessed wall switches.

E. Coordinate requirements for metal supports required for smoke-protective curtain assemblies.

1.4 ACTION SUBMITTALS
Action submittals are submittals requiring responsive action and return of reviewed documents to Contractor.
A. Product Data: For each type of smoke-protective curtain assembly and draft curtain.

1. Include construction details, material descriptions, dimensions of individual components and profiles, and finishes for smoke curtains.

2. Include points of attachment and their corresponding static and dynamic loads imposed on structure.

Retain subparagraph below for power-operated smoke curtains.

3. Include ratings, operating components, electrical characteristics, control systems, and furnished specialties and accessories.

B. Shop Drawings: For each installation and for special components not dimensioned or detailed in manufacturer's product data.

1. Include plans, elevations, sections, and attachment details.

2. Include details of smoke curtain assemblies. Indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location of each field connection.

3. Include points of attachment and their corresponding static and dynamic loads imposed on structure.

4. Detail fabrication and assembly of smoke-protective curtain assemblies.

5. Show locations of controls, detectors, and other accessories.

Retain subparagraph below if equipment includes wiring.

6. Include diagrams for power, signal, and control wiring.

C. Product Schedule: For smoke curtain assemblies.
[ Use same designations indicated on Drawings.]

1.5 INFORMATIONAL SUBMITTALS

Informational submittals are submittals that require review by Architect, but they do not require Architect's responsive action and return of reviewed documents to Contractor, provided submittals comply with requirements. If rejected, submittals with responsive action must be returned to Contractor.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

A. Qualification Data: For Installer, manufacturer, testing agency, and factory-authorized service representative.

For hospital projects located in the state of California, include OSHPD Preapproval of Manufacturer's Certification (OPM) and OSHPD Special Seismic Certification Preapproval (OSP).

For OSHPD, see https://oshpd.ca.gov/construction-finance/preapproval-programs.
B. Evaluation Reports: For curtain assemblies, from ICC-ES ESR-4761 

1.6 CLOSEOUT SUBMITTALS

A. Operation and Maintenance Data: For smoke curtain assemblies to include in emergency, operation, and maintenance manuals.

B. Field quality-control reports for required testing.

1.7 QUALITY ASSURANCE

A. Manufacturer Qualifications: An entity experienced in manufacturing smoke-and-draft-control curtain assemblies that have been successfully installed in compliance with requirements of authorities having jurisdiction.

B. Installer Qualifications: An entity that employs installers and supervisors who are trained and approved by manufacturer for both installation and maintenance of units required for this Project.

C. Smoke-Protective Curtain Assembly Inspector Qualifications: Inspector for field quality control inspections of smoke-protective curtain assemblies complying with NFPA 105.

1.8 FIELD CONDITIONS

A. Field Measurements: Field-verify and coordinate dimensions and indicate measurements on Shop Drawings.

Door Systems provides a standard 1-year warranty.
PART 2 -  PRODUCTS

Manufacturers and products listed in this Section are neither recommended nor endorsed by the AIA or Deltek. Before selecting manufacturers and products, verify availability, suitability for intended applications, and compliance with minimum performance requirements. Product options commonly available from manufacturers are included in square brackets throughout the Section Text. Not every manufacturer listed can provide every option offered; verify availability with manufacturers. For definitions of terms and requirements for Contractor's product selection, see Section 016000 "Product Requirements."
2.1 MANUFACTURERS, GENERAL

A. Source Limitations: Obtain smoke-protective curtains from single source from single manufacturer.

Retain subparagraph below or revise to suit Project.

1. Obtain operators and controls from smoke-protective curtain manufacturer.

2.2 PERFORMANCE REQUIREMENTS
Retain "Smoke-Protective Curtain Assemblies" Paragraph below for smoke-protective curtain assemblies without fire-protection rating. Overhead coiling curtains are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 ft. 6 inches (4.11 m).

A. Smoke Protective Curtain Assemblies: Provide smoke-protective curtains that are listed and labeled with the letter "S" on the rating label by a qualified testing agency for smoke- and draft-control based on testing in accordance with UL 1784; with maximum air-leakage rate of 3.0 cfm/sq. ft. (0.01524 cu. m/s x sq. m) of opening at 0.10 inch wg (24.9 Pa) for both ambient and elevated temperature tests.
Retain "Smoke- and Fire-Protective Curtain Assemblies" Paragraph below if applicable. Overhead coiling curtains are labeled by UL for sizes not exceeding 152 sq. ft. (14 sq. m), with no dimension exceeding 13 ft. 6 inches (4.11 m).

Retain "Electrical Components, Devices, and Accessories" Paragraph below for operable curtain assemblies.

B. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

Retain "Seismic Performance" Paragraph below if seismic design of draft curtains is required for Project. Revise to indicate specific loads determined by Project's structural engineer, or refer to loads indicated on Drawings. Model building codes and ASCE/SEI 7 establish criteria for buildings and components subject to earthquake motions. Coordinate requirements with Project's structural engineer.

For hospital projects located in the state of California, include OSHPD Preapproval of Manufacturer's Certification (OPM) and OSHPD Special Seismic Certification Preapproval (OSP).

For OSHPD, see https://oshpd.ca.gov/construction-finance/preapproval-programs.
2.3 SMOKE-PROTECTIVE CURTAIN ASSEMBLIES FOR ELEVATOR ENTRANCES

A. Alarm-activated smoke curtain assembly complying with ICC-ES AC77.

Door Systems' "Model DSI-600 with Vision Panel Elevator Smoke Containment System" offers gravity fail-safe performance. The curtain remains virtually invisible in the retracted position within the compact head-box. When signaled by a local detector or fire alarm system, the curtain descends to the operational level using the gravity fail-safe system. The addition of the vision lite into this elevator smoke containment system will satisfy section 2.11.6.3 (d) of the ASME A17.1 Elevator Code. When in the closed position, the addition of the vision lite allows firefighters to observe the elevator landing (lobby) when the elevator hoistway door is no more than one-quarter open.

For "Model DSI-600 Elevator Smoke Containment System," see www.doorsysinc.com/smoke-and-fire-curtains/elevator-smoke-containment-system or call (866) 534-3667.
Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to require a specific product or a comparable product from manufacturers listed.

B. Basis-of-Design Product: Subject to compliance with requirements, provide Door Systems; Model DSI-600 Elevator Smoke Containment System:
1. Door Systems Inc, Placentia, CA www.doorsysinc.com
C. Smoke Containment: Assemblies complying with UL 1784 for air leakage.

Select second option in first paragraph below for Door Systems' non-fire-rated models.

D. Curtain: Manufacturer's standard glass-fiber fabric with Vision Lite per Section 2.11.6.3 (d) of ASME A17, and ICC ESR-4761 Report- AC 77 Criteria 
E. Operation: Controlled descent automatically by fail-safe gravity deployment and motorized rewind.

F. Curtain Attachment: Curtain will form a pressure-resisting seal.
Retain "Captured Side Guides" Subparagraph below for Door Systems' "Model DSI-600 Elevator Smoke Containment System".

1. Captured Side Guides: Formed from factory-primed galvanized-steel sheet complying with ASTM A653/A653M with integral pressure-retaining tabs.

G. Control System: Provide factory-assembled control unit as required for assembly specified.

1. Fail-safe, gravity-closing device with battery backup deploys on activation of building fire alarm or testing key switch in compliance with UL 864.

2. Curtain Rewind Switch: Include a switch to rewind the screen into housing.

3. Motor Operator: Provide factory-assembled electric operation system of size and capacity recommended in writing by curtain manufacturer for assembly specified, with electric motors and factory-prewired motor controls, control devices, and accessories required for proper operation.

4. Electrical Components, Devices, and Accessories: Listed and labeled in accordance with NFPA 70, by a qualified testing agency, and marked for intended location and application.

H. Housing Type: Sheet metal housings containing support rollers and associated electronics.

1. Coordinate operator wiring requirements and electrical characteristics with the building electrical system.

PART 3 -  EXECUTION
3.1 EXAMINATION

A. Examine substrate areas and conditions, with Installer present, for compliance with requirements for substrate construction and other conditions affecting performance of the Work.

B. Examine locations of electrical connections.

C. Proceed with installation only after unsatisfactory conditions have been corrected.

3.2 INSTALLATION

Retain "Smoke- and Fire-Protective Curtains" Paragraph below if required.

Retain "Smoke-Protective Curtains" Paragraph below if required.

A. Smoke-Protective Curtains: Install smoke-protective curtain assemblies in accordance with manufacturer's written installation instructions and NFPA 105.

B. Install anchorage devices to securely fasten assembly to substrate and building framing without distortion or stress.

C. Securely brace components suspended from structure.

D. Fit and align assembly.

Retain "Field Quality Control" Article for operable curtain assemblies.

3.3 FIELD QUALITY CONTROL

Retain "Testing Agency" Paragraph below to identify who will perform tests and inspections. If retaining second option below, retain "Field quality-control reports" Paragraph in "Informational Submittals" Article.

A. Testing Agency: Owner will engage a qualified opening protective assembly inspector to perform tests and inspections and to furnish reports to Architect.

B. Perform the following tests and inspections with the assistance of a factory-authorized service representative:
1. Test release mechanism, closing, and alarm operations when activated by smoke detector or building's fire-alarm system. Test manual operation of closed curtain. Reset closing mechanism after successful test.

2. Inspections: Inspect each smoke-protective curtain assembly in accordance with NFPA 105.

C. Repair or remove and replace installations where inspections indicate that they do not comply with specified requirements.

D. Reinspect repaired or replaced installations to determine if replaced or repaired door assembly installations comply with specified requirements.

E. Prepare and submit a separate inspection report for each smoke-protective curtain assembly indicating compliance with each item listed in NFPA 105.

3.4 DEMONSTRATION

A. Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain overhead coiling smoke curtains.

3.5 MAINTENANCE

A. Engage a manufacturer's authorized service representative to test, adjust, and maintain the smoke-protective assemblies once per year, as required by NFPA 105.

END OF SECTION 083343
	OVERHEAD COILING SMOKE CURTAINS
	083343 - 1



