# SECTION 08 34 90

**DEPLOYABLE FABRIC FIREWALL**

**PART 1 - GENERAL**

## SUMMARY

* + 1. Section Includes: A Fire, Smoke, and Temperature-Rise-Rated fabric fire wall curtain system designed to act as a movable fire wall.
    2. Products Supplied but Not Installed Under This Section:
       1. Group Control Panel unit.
       2. Emergency Up Buttons (optional)
    3. Related Sections:
       1. 09 2200Non-Load Bearing and Load Bearing Wall Framing: Metal backing in housing and jamb mounting areas.
       2. 09 9100Paints: Field painting of specified components.
       3. 28 3000Detection and Alarm: Provision of smoke detectors.
       4. Division 26 Sections for 120VAC and 24V control circuit power, including conduit, boxes, conductors, wiring devices, and emergency power.
       5. 08 3100 Access Panels

## REFERENCES

* + 1. ASTM E84-10 test report with calculated smoke development (CSD) of 2 and a smoke-developed index (SDI) of 0, and a calculated flame spread (CFS) of 0.
    2. NFPA Codes and Standards:
       1. 70  National Electrical Code.
       2. 105  Recommended Practice for the Installation of Smoke-Control Door Assemblies.
       3. ASTM – E84 Test report with Calculated Smoke Developed (CSD) of 2 and a Smoke Developed Index (SDI) of 0 and a Calculated Flame Spread (CFS) of 0.
    3. UL Minimum Performance Standards
       1. UL 263/ASTM E-119 for fire partitions
       2. UL 10B Fire test for door assemblies with ASTM E2226 hose stream test
       3. UL Oversized Certificate where units exceed the testing laboratory’s label size
       4. UL 1784  Air Leakage Tests for Door Assemblies.
       5. UL 864 – Classified Control Units for Fire Protective Signaling Systems
       6. Gravity fail-safe design. No battery back-up will be required for deployment.
       7. Certified to ISO 9001 1994 for the design, manufacturing, installation, and commissioning of Automatic Smoke and Fire Barriers and Partitions.
       8. Accredited testing lab follow up service report required.

## SUBMITTALS

* + 1. Product Data: For each type of product
       1. Shop Drawings: Show fabrication and installation details for deployable fabric fire wall curtains. Include plans, sections details, attachments to other work and the following:

1. Operating clearances
2. Requirements for supporting deployable fabric fire wall curtains, track, equipment.
3. Locations of equipment components, switches, motors and controls. Differentiate between manufacturer-installed and field installed wiring.
   * + 1. Quality Assurance/Control Submittals:
4. Certifications: Copy of specified items.
5. Manufacturer’s installation instructions and testing procedures

## CLOSEOUT SUBMITTALS

* + 1. Comply Section 01 7700Closeout Submittals; submit following items:
       1. Operation and Maintenance Manual
       2. Manufacturer’s Warranties

## QUALITY ASSURANCE

* + 1. Overall Standards:
       1. Provide units tested, approved, and labeled under UL263/ASTM E119
       2. UL10B with ASTM E 2226 Hose Stream
       3. UL 1784 standards
       4. UL 864 – Classified Control Units for Fire Protective Signaling Systems
       5. Accredited testing laboratory follow up Service Report
       6. Testing laboratory’s label permanently affixed to bottom bar
    2. Qualifications:
       1. Manufacturer Qualifications: Minimum five years’ experience in producing smoke and fire rated curtain systems.
       2. Installer Qualifications: Factory trained by manufacturer.
    3. Certification:
       1. UL accredited Testing Laboratory Label for UL263 and ASTM E119
       2. Oversized certificate labeled, listed, classified, certified, and marked where units exceed testing laboratory’s label size.
    4. Pre-Installation Meeting:
       1. Schedule and convene a pre-installation meeting prior to commencement of field operations with representatives of the following in attendance: Owner, Architect, General Contractor, smoke containment system sub-contractor, painting sub-contractor, and electrical sub-contractor.
       2. Review substrate conditions, requirements of related work, installation instructions, storage and handling procedures, and protection measures.
       3. Keep minutes of meeting including responsibilities of various parties and deviations from specifications and installation instructions.

## DELIVERY, STORAGE, AND HANDLING

* + 1. Reference Section 01 6600Product Storage and Handling Requirements.
    2. Follow manufacturer’s instructions.

## WARRANTY

* + 1. Provide manufacturer’s standard one-year warranty.
    2. Maintenance and Testing:
       1. Perform minimum annual maintenance and testing on each smoke and fire containment system as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.
       2. Provide test documentation.

# PART 2 - PRODUCTS

## MANUFACTURER

Model DSI-FW119 Deployable Fabric Fire Wall

Manufacturer: DSI Smoke and Fire Curtains www.doorsysinc.com 866-534-3667

Label each firewall system with the following information:

Manufacturer’s name.

Temperature rise rating: Not more than 250 degrees Fahrenheit above ambient after 120 minutes of standard fire exposure.

* + - 1. Provide units tested, approved, and labeled under UL263/ASTM E119
      2. Label of quality control agency.

## 2.02 PERFORMANCE REQUIREMENTS

UL263/ASTM E119 Listed and labeled for use as a 2-hour movable firewall.

Temperature rise rating: Not more than 250 degrees Fahrenheit above ambient after 120 minutes of standard fire exposure.

## 2.03 COMPONENTS

The curtain head boxes shall be manufactured from 1.2mm galvanized steel. The enclosures shall be rated at the same temperature as the curtain fabric. Two curtain headboxes are installed back-to-back with a minimum gap of 12” between the deployable curtain fabric to achieve a temperature rise rating per ASTM E119/UL263.

Removable cover plates shall be incorporated to allow access to the curtain rollers.

Standard head box sizes for single rollers (maximum width 16’-0”) and for multiple rollers (over 16’-0” wide). Larger head boxes may be required where the fabric firewall drop is more than 10’-0”. Primed steel finish

Side guide rails shall be 3” deep x 4” wide, primed steel finish.

Weighted bottom bars shall be provided to prevent deflection and ensure correct operation under gravity.

The rollers shall be constructed from an octagonal tube which will incorporate a 208v motor and gearbox and a sealed heavy-duty ball bearing assembly.

A motor control circuit housed in a steel enclosure shall be mounted onto the motor end of each head box.

Provide each motorized curtain with a back Electromagnetic force-controlled speed of descent of no less than 6 inches per second and no more than 24 inches per second.

The deployable fabric fire wall shall be manufactured from multiple layers of woven glass cloth,wired mesh and insulation.

## 2.04 OPERATION

In an emergency situation, the deployable fabric fire wall system shall deploy upon a signal from the fire alarm system.

The system must be proven to “fail safe” to the operational position on total loss of primary and auxiliary power.

Under normal operating conditions the curtains would be held in the retracted position via the motors operating at 208 voltage. The manufacture must be able to confirm that the motor windings are suitable for this type of operation.

Upon activation of the fire alarm the control panel will remove the supply voltage and the fabric fire wall shall descend under the power of gravity in a controlled manner. A dynamic braking system housed in the motor control circuit shall control the speed of the descent of the curtain. The descent shall be electronically synchronized on overlapping curtains with a bottom bar.

To retract the fabric fire wall the control panel shall supply power to the motor control circuits and motors will drive the curtains to the upper position. As the bottom bar or stopping bar hits the curtain head box a current limiting circuit will step back the voltage and current and hold the bottom bar in the retracted position.

Should the main power fail to the group control panel, the supply is automatically switched to the integral standby battery. The fabric fire wall remains in the retracted position for 1 hour (fully retracted loaded system).

Group Control Panel: Should smoke be detected, the fire alarm contact in the GCP will be opened by the fire alarm control system, the GCP will remove the power supply to the curtain motors and the curtains will descend under the power of gravity in a controlled manner.

Open on fire- configured to be gravity fail safe.

Test Facility switch required.

# PART 3 - EXECUTION

## EXAMINATION

* + 1. Examine substrates upon which work will be installed.
       1. Verify related work performed under other sections is complete and in accordance with Shop Drawings.
       2. Verify wall surfaces are acceptable for deployable fabric firewall system components installation.

## INSTALLATION

* + 1. Install deployable fabric firewall components in accordance with the manufacturer’s installation instructions.

## FIELD QUALITY CONTROL

* + 1. Field Test: Follow the manufacturer’s cycle test procedures.
       1. Notify the Owner’s Representative, the local Fire Marshal, and the alarm subcontractor at least one week before scheduled testing.
       2. Complete maintenance service record.

## DEMONSTRATION

* + 1. Demonstrate required testing and maintenance procedures to Owner’s Representative.
    2. Maintenance and Testing:
       1. Perform minimum annual maintenance and testing on each deployable fabric firewall system as required by the manufacturer’s warranty, code agency evaluation reports, and as required by the local authority having jurisdiction.
       2. Retain a permanent record of tests.
    3. Qualified Door Systems, Inc Inspector assesses unit(s) after exposure to a fire event.

## MAINTENANCE

* + 1. Engage a Door Systems authorized service representative to test, adjust, and maintain the system once per annum as required per NFPA 101 and NFPA 80.

END OF SECTION 08 34 90