SPECIFICATIONS: FIREGUARD MFW

SECTION: 10 22 33 – ACCORDION FOLDING FIRE PARTITIONS – MOVEABLE FIRE WALL

#### PART 1 – GENERAL

#### 1.01	SUMMARY OF WORK

- Division 0 and 1, as indexed, apply to this section.

Furnish and install all horizontal sliding, accordion folding fire partitions shown on the drawings and specified herein.

#### 1.02	RELATED SECTIONS

- All headers, support structures, fire protection of support structures, surrounding insulation, jambs, storage pockets, pocket doors, access doors, blocking and trim shall be furnished and installed by other sections.

All electrical wire, wiring, conduit and electrical boxes shall be furnished and installed by electrical section including connections to smoke detectors and building fire alarm panels.

Drilling/placement of anchorage points into pre or post tensioned decks, welding/ punching/drilling steel members and all drywall work.

OPTION: All track, soffit, chain guide and wall mounted striker posts shall be painted by Section 09 90 00. Color shall be selected by the architect.

OPTION: If Section 2.04 C, Individual Door Status Display, is selected as an option, the following paragraph should be included:  Wiring for Individual LCD Door Status Display at fire partition-One (1) USOC RJ14-6POS 4 wire jack shall be supplied at the back of the storage pocket and shall be tied to the 4 square junction box adjacent to the partition with CAT 5 twisted 2 pair cable.  The junction box, RJ14 jack and wire shall be furnished and installed by the electrical section.  Termination to the LCD panel shall be by punch down block and shall be by the electrical section as per the manufacturer’s instructions.

#### 1.03	QUALITY ASSURANCE

- Installation shall be performed by factory trained and certified installers with a minimum of three years’ experience installing electrically operated accordion folding fire partitions.

- Doorsysinc.com 714-258-7100

Fire partitions shall be listed by Underwriters Laboratories for ratings as indicated, when tested in accordance with the requirements of UL 263 and ASTM E-119.

Automatic closing system shall be listed by Underwriters Laboratories in accordance with the requirements of UL 864 and be listed for use with assembly in compliance with NFPA 80.

- 1.04	SUBMITTALS

- Refer to Section 01 30 00 – Administrative requirements for shop drawings and submittals.

- Product Data: Provide manufacturer’s technical literature, include UL listing data.

- Shop Drawings:  Indicate construction and installation details and dimensions, including layout, electrical requirements, required stacking depth, height of header above finished floor, and requirements for anchorage and support of each fire partition.

Operation and Maintenance Data: Operating procedures, troubleshooting and repair methods, and wiring diagrams.

#### 1.05	DELIVERY, STORAGE, AND HANDLING

- Door Systems will deliver original, unopened packages to a location designated by the General Contractor. Deliver to the job site in manufacturer's original, unopened package.

#### 1.06	COORDINATION BY GENERAL CONTRACTOR

- Coordinate with the following:

  - Fire Alarm System.

  - Electrical.

  - Pocket cover door (if required).

  - Floor and ceiling finish.

- Assure accurate installation of header, jamb, and trim.  Provide “As-Built” dimensions for opening and storage pocket.  Supervise unloading and handling of materials.

Store boxes flat (not more than three high) in a dry area and protect from elements that may damage materials.

Permanent power shall be in-place and ready for final connection when fire partitions are erected. Assure access to and proper clearance for motor operators.

After testing the fire alarm system, automatic-closing fire partitions shall be re-set to the original position.

#### 1.07	WARRANTY

- Materials and installation shall be warranted against defects in workmanship for a period of two (2) years from the date of substantial completion.

#### PART 2 – PRODUCTS

#### 2.01	MANUFACTURER AND MODEL

- Accordion folding fire partition shall be Won-Door FireGuard Moveable Fire Wall model MFW____ (select one: 1 or 2 – number designates hours of fire rating) as manufactured by Won-Door Corporation, and supplied and Installed by Doorsysinc.com 714-258-7100.

No substitutions allowed.

#### 2.02	ACCORDION FIRE PARTITIONS - GENERAL

- Provide power operated self-closing fire partitions of configurations indicated on the drawings.

  - Fire rating as required.

- Fire Rating:  Fire partitions shall be listed by Underwriters Laboratory as special purpose fire partitions having a (select one: 1 or 2) hour fire protection rating in accordance with the requirements of UL 263 and ASTM E-119.

Closing and Opening Operation:  Automatic Closing System including motor operator and releasing devices shall be a Microprocessor-based system rated to UL864 (Releasing Device Control Unit) and shall commence closing upon activation by fire alarm system and/or by low battery voltage.

  - Obstruction Detection:  Contact with an obstruction shall cause the partition to stop, reverse enough to remove pressure on the leading edge, pause, and then re-close when in an alarm condition.

  - Constant pressure to the leading edge while not under motor power shall prevent motor operation and allow the partition to be opened manually.

#### 2.03	COMPONENTS

- Partition Construction:  Two parallel, accordion-type walls of panels independently suspended with no floor tracks, pantographs, or interconnections except at the lead-post.

  - Panels: 24-gauge steel; V-grooved; modular design; capable of in-place repair.

  - Perimeter Seals: shall consist of continuous extruded sweeps attached to the top and bottom of the fire partition to form a smoke and draft seal.

  - Hanging weight shall be 6.5 pounds per square foot when extended across the opening.

  - Finish:  All steel panels shall have factory applied protective coatings.

  - Color:  Manufacturer’s standard platinum.

Suspension System: Two tracks, on 8-inch centers, attached to overhead structural support.

  - Tracks: 14 gauge cold rolled steel.

  - Panel hangers: Each panel suspended from a steel hanger pin and a ball bearing roller.

  - Lead post hangers:  8-wheel ball bearing trolley.

Power Supply: 120-volt power source to power supply for main power.  On loss of AC power, the 12v/24v secondary power source shall provide full operation capability.

Automatic Closing System shall be listed to UL864 including capability to send and receive signals from the Fire Control Panel and shall consist of the following:

  - Microprocessor based Electronic Control box with the ability to:

    - Monitor dual power sources continually for peak performance including:

      - Detect a missing battery, bad battery, or low battery condition.

      - Detect if the charging circuit is bad.

      - Detect fuse failures.

      - Detect high or low AC conditions.

    - Monitor the health of the drive train.

    - Monitor inputs including faults associated with door block, exit hardware, patron hardware, and key switches.

    - Run a “watch dog” monitoring circuit which will force a software restart in the event the software hangs, including tracking the number of resets that occur for diagnostic purposes.

    - Withstand voltages up to 120 volts AC on the fire alarm input circuit without damage including the ability to indicate that the alarm circuit has not been wired as a dry contact, “no voltage” circuit when errant voltages are applied to the circuit.

    - Communicate with other microprocessors in the assembly via an internal bus system.

    - Indicate faults or supervised information both locally and at a remote location.

  - Motor Operator Assembly including a DC gear-motor, drive sprocket, clutch, and position sensors.  The motor shall drive the fire partition by means of a chain attached to a stabilizer bar trolley.

  - A partition control momentary rocker switch shall be mounted on one side of the partition and shall function as follows:

    - Pressing the upper portion of the switch shall close the partition and/or clear fault conditions.

    - Pressing the lower portion of the switch shall open the partition and/or temporarily mute the local horn.

  - Leading Edge shall be pressure sensitive such that contact with an obstruction shall cause the partition to stop, pause for 3 seconds, and then re-close when in an alarm mode.

- 2.04	OPTIONS

- Key Switch Module shall be provided by Won-Door.

- Exit Device provided on both sides of the Moveable FireWall.

- Individual Door Status Display panel shall be provided adjacent to the partition to indicate in the English language the status of the partition, i.e., door position and trouble conditions.  It shall have a port that allows easy access to a diagnostic tool for the purposes of field programming the partition to customized settings.  (Note: Electrical requirements for the Individual Door Status Display panel can be found in Section 1.02 E)

- Obstruction Detector An infrared light beam shall be provided to monitor the opening path.  If an object is placed in the path of the partition for more than 4 minutes, the beam shall cause the door to sound an alarm indicating a path obstruction.

- Auxiliary Relay Module (XRM) can provide two additional output relays to indicate specific status and fault conditions including any two of the following:  Open, Opening, Closed, Closing, Stopped, Locked, Exit Hardware Access, Secure Access, Forced Entry, TLS Failure, Key Switch Failures, Stuck Switches, Power Failures, Communication Errors.

#### 2.05	RELATED CONSTRUCTION

- Track Support Construction: Provide supports attached to structure and mounting surface for track including drilling/placement of anchorage points into pre or post tensioned decks, welding/punching/drilling steel members, and all drywall work; comply with partition manufacturer’s instructions and recommendations.  Headers furnished & installed by the general contractor or other sections, shall be parallel with the finished floor within +/- 1/8” tolerance over the entire length of the opening.

- Pocket Construction:  Provide rated pocket as specified for storage of accordion folding fire partition when open; comply with partition manufacturer’s instructions and recommendations.

- Pocket Door:  Maintain full pocket clear width when pocket door is open.

- Striker Recess: Mount 16-gauge steel striker in wall recess deep enough to prevent striker from protruding beyond face of wall; construct recess to maintain fire rating of wall.

- Protection: Protect installed work from damage.

#### PART 3 – EXECUTION

#### 3.01	EXAMINATION

- Verify that adjacent construction is suitable for installation of partition.

- Verify that electrical utilities have been installed and are accessible.

- Verify that partition opening is plumb, and header is parallel with the finished floor.

- Verify clear opening dimensions.

- Notify Architect/ General Contractor of any unacceptable conditions or varying dimensions.

#### 3.02	INSTALLATION

- Install fire partitions in accordance with manufacturer's instructions, shop drawings, and NFPA 80.

Install fire partitions plumb and parallel with the finished floor.

Installation shall be performed by factory trained and certified installers with experience installing electrically operated accordion folding fire products.

#### 3.03	ADJUSTING

- Adjust door installation to provide uniform clearances and smooth, quiet, non-binding operation.

- Test that all operations are functional and meet the requirements of local codes.

#### 3.04	CLEANING

- Clean surfaces using manufacturer’s recommended means and methods.

- 3.05	STORAGE OF WASTE AND RECYCLING

- Store and recycle waste in accordance with Section 01 74 19 Construction Waste Management and Disposal.

- 3.06	MAINTENANCE

- A. Engage a Door Systems, authorized service representative, Doorsysinc.com 714-258-7100, to test, adjust and maintain the system once per annum as required per NFPA 101 and NFPA 80.

END OF SECTION 08 22 33