DIVISION 08 - OPENINGS

SECTION 08 35 13.23 – ACCORDION-FOLDING FIRE DOORS (FireGuard Slim)

# PART I – GENERAL

#### SUMMARY

- WORK INCLUDED:

  - Division 0 and 1, as indexed, apply to this section.

  - Furnish and install all horizontal-sliding, accordion-folding doors to meet manufacturer’s specifications & applicable codes, shown on the drawings and specified herein at the time of purchase.

- RELATED WORK:

  - Division 9: All track, soffit, chain guide and strikers shall be painted by Section 09 90 00. Color shall be selected by the architect.

  - Division 26: All electrical wire, wiring, conduit and electrical boxes shall be furnished and installed by electrical section, including connections to smoke detectors and building fire & access control alarm panels.

#### REFERENCES

- UNDERWRITERS LABORATORIES, WHERE APPLICABLE

  - UL 10B: Standard for Safety – Fire Tests of Door Assemblies

  - UL 10C: Standard for Positive Pressure Fire Tests of Door Assemblies

  - UL 864: Control Units and Accessories for Fire Alarm Systems

  - UL 1784: Standard for Air Leakage Tests of Door Assemblies and Other Opening Protectives

- NATIONAL FIRE PROTECTION ASSOCIATION, WHERE APPLICABLE

  - NFPA 72: National Fire Alarm and Signaling Code

  - NFPA 80: Standard for Fire Doors and Other Opening Protectives

  - NFPA 101: Life Safety Code

  - NFPA 105: Standard for Smoke Door Assemblies and Other Protective Openings

  - NFPA 252: Standard Methods of Fire Tests of Door Assemblies

- NATIONAL RESEARCH COUNCIL CANADA (NRCC), WHERE APPLICABLE

  - National Building Code of Canada (2020)

  - National Fire Code of Canada (2020)

- INTERNATIONAL BUILDING CODE (2009, 2012, 2015, 2018, 2021), WHERE APPLICABLE

- INTERNATIONAL FIRE CODE (2009, 2012, 2015, 2018, 2021), WHERE APPLICABLE

- CALIFORNIA BUILDING CODE (2019), WHERE APPLICABLE

- CALIFORNIA FIRE CODE (2019), WHERE APPLICABLE

- AMERICAN SOCIETY OF MECHANICAL ENGINEERS (ASME), WHERE APPLICABLE

#### 1.03	QUALITY ASSURANCE

- Installation shall be performed by factory trained and certified installers with experience installing electrically operated, accordion folding doors.

- Doorsysinc.com 714-258-7100

Doors with a fire rating shall be listed by Underwriters Laboratories for ratings as indicated, when tested in accordance with the requirements of UL 10B and NFPA 252.

Automatic closing system shall be listed by Underwriters Laboratories in accordance with the requirements of UL 864 and in compliance with NFPA 80.

Doors used for smoke and draft control shall bear the “S” mark on the door UL label and shall have an air leakage of less than 3 CFM/ft2 at 0.1 inch of water column pressure when tested in accordance with UL 1784 with an artificial bottom seal.

Doors shall be capable of resisting an air pressure differential up to 0.05 inches of water column.  Optional air pressure resistance up to 0.10 inches of water column available.

CERTIFICATIONS

  - International Code Council – Evaluation Service (ICC-ES)

    - Evaluation Service Report – 1394 (ESR – 1394)

  - Factory Mutual Insurance Company (FM Global)

  - California Department of Forestry & Fire Protection (CalFire)

    - Building Materials Listing Program

      - FireGuard (models 20, 60 and 90)

#### 1.04	SUBMITTALS

- See Section 01 30 00 – Administrative Requirements, for submittal procedures.

- Product Data: Provide manufacturer’s technical literature, include UL listing data.

- Shop Drawings:  Indicate construction and installation details and dimensions, including layout, electrical requirements, required stack depth, height of header above finished floor, and requirements for anchorage and support of each door.

- Operation and Maintenance Data:  Operating procedures, troubleshooting and repair methods, and wiring diagrams.

- Closeout Submittals: Owner’s manual and warranty documentation as specified herein.

#### 1.05	DELIVERY, STORAGE, AND HANDLING

- Door Systems will deliver original, unopened packages to a location designated by the General Contractor.  All packages must be stored indoors, protected from moisture damage and secure from theft or other damage.  General Contractor to note any damage or shortages at time of delivery.

#### 1.06	COORDINATION BY GENERAL CONTRACTOR

- Coordinate with the following:

  - Electrical.

  - Fire Alarm system (if required).

  - Access Control wiring (if required).

  - Floor and ceiling finish.

  - Structural support and adjacent, rated wall construction.

- Assure accurate installation of header, jamb, and trim.  Provide “As-Built” dimensions for opening and storage pocket.  Supervise unloading and handling of materials.

- Store boxes flat (not more than three high) in a protected dry area.

- Permanent power shall be in-place and ready for final connection when doors are installed. Assure access to and proper clearance for motor operators.

- Access control doors shall be reset after being tested for proper security application.  After testing the fire alarm system, if applicable, automatic-closing fire doors shall be re-set to the original position.

#### 1.07	WARRANTY

- Materials and installation shall be warranted against defects in workmanship for a period of two (2) years from the date of substantial completion.

#### PART 2 – PRODUCTS

#### 2.01	MANUFACTURERS

- Horizontal-sliding, accordion-folding, fire doors as manufactured by Won-Door Corporation and supplied and Installed by Doorsysinc.com 714-258-7100 shall be specified as the following:

Won-Door FireGuard Slim____

  - Fire rating:

{Choose One}:

    - ‘S’ rating only

    - 20 Minutes

    - 60 Minutes

    - 90 Minutes

- No substitutions allowed.

#### 2.02	ACCORDION FIRE DOORS – GENERAL

- Provide electrically powered self-closing fire doors of configurations indicated on the drawings.

- Fire rating as required.

- Maximum opening width for this model is 9’-0”.  The opening height shall be specified as:

{Choose 1}:

    - 7’ 0”

    - 8’ 0”

For fire doors exceeding these sizes, requiring temperature rise rating (TR), curves or a bi-parting configuration, please refer to Doorsysinc.com 714-258-7100 for further design assistance.

- Fire Rating – Fire doors shall be listed by Underwriters Laboratory as special purpose fire doors having a {Choose One}: ‘S’ rating, 20-, 60- or 90-minute fire protection rating in accordance with the requirements of UL 10B and NFPA 252.

- Closing and Opening Operation:  Automatic Closing System, listed to UL864 including motor operator and releasing devices shall be a Microprocessor-based system and shall commence closing upon activation by fire signal, access control signal, low battery voltage or optional low AC voltage.

- Obstruction Detection:  Contact with an obstruction shall cause the door to stop, reverse enough to remove pressure on the leading edge, pause, and then re-close when in an alarm condition.

- Constant pressure to the leading edge while not under motor power shall prevent motor operation and allow the door to be opened manually.

- Exit Device Operation: Provide an exit device on one or both sides of door.  Location for exit devices is at the leading edge.

  - In emergency mode, a slight pressure on the exit device will cause the door to open a field-programmable distance, up to the entire opening width, pause for a field-programmable duration between 3 and 30 seconds, and then automatically close.

2.	The exit device shall have the ability when not in the emergency (fire) mode to be used to open the door and move it back into the storage pocket.

#### 2.03	COMPONENTS

- Door Construction: Two parallel, accordion-type walls independently suspended with no floor tracks or pantographs.

- Panels: 24-gauge steel, V-grooved; modular in design; capable of in-place repair.

- Perimeter Seals: shall consist of continuous extruded sweeps attached to the top and bottom of the fire door to form a smoke and draft seal.

- Hanging Weight: 5.5 pounds per sq. ft. when extended across opening.

- Finish: All steel panels shall have factory-applied protective coatings.

- Color: Manufacturer’s standard platinum.

- Suspension System: Two tracks, on 8-inch centers, attached to overhead structural support.

- Track: 1/8” extruded aluminum.

- Panel Hangers:  Panels shall be suspended by a steel hanger pin and ball bearing roller system.

- Power source shall be: 120 – 240-volt AC input.  System operation voltage shall be dual sourced from DC power supply and backup battery.

- Automatic Closing System shall be listed to UL864 including capability to send and receive signals from the Fire Control Panel and/or Access Control System, and shall consist of the following:

- Microprocessor based Electronic Control box with the ability to:

- Monitor dual power sources continually for peak performance including:

      - Detect a missing battery, bad battery, or low battery condition.

      - Detect if the charging circuit is bad.

      - Detect fuse failures.

      - Detect high or low AC conditions.

- Monitor the health of the drive train.

- Monitor inputs including faults associated with door block, exit device and patron hardware.

- Run a “watch dog” monitoring circuit which will force a software restart in the event the software hangs, including tracking the number of resets that occur for diagnostic purposes.

- Withstand aberrant voltages up to 120 volts AC on the fire alarm input circuit without damage including the ability to indicate that the alarm circuit has not been wired as a dry contact, “no voltage” circuit when errant voltages are applied to the circuit.

- Communicate with other microprocessors on the system via an internal bus system.

- Indicate faults or supervised information both locally and at a remote location.

      - Motor Operator Assembly including a DC gear-motor, drive sprocket, clutch, and position sensors.  The motor shall drive the door by means of a chain.  Standard motor drive speed will be approximately 9” per second.

      - Leading Edge assembly shall be pressure sensitive such that contact with an obstruction shall cause the door to stop, pause for a minimum of 3 seconds, then re-close when in alarm mode.

      - Exit Device will be located on each side of the door.

- The header shall be provided as an integrated part of the door assembly and shall Include track, threaded rods and mechanical attachment hardware.

#### 2.04     RELATED CONSTRUCTION

- All headers, support structures, fire protection of support structures, surrounding insulation, jambs, storage pockets, blocking and trim shall be furnished and installed by other sections.

- All electrical wire, wiring, conduit and electrical boxes shall be furnished and installed by electrical section, including connections to smoke detectors and building fire and access control alarm panels.

- Drilling/placement of anchorage points into pre- or post-tensioned decks, welding/ punching/drilling steel members and all drywall work by other sections.

- Track Support Construction:  Provide supports attached to structure and mounting surface for track including drilling/placement of anchorage points into pre or post tensioned decks, welding/punching/drilling steel members, and all drywall work; comply with door manufacturer’s instructions and recommendations.

- Pocket Construction:  Provide rated pocket as specified for storage of accordion door when open; comply with door manufacturer’s instructions and recommendations.

- Protection: Protect installed work from damage.

#### PART 3 – EXECUTION

#### 3.01	EXAMINATION

- A. 	Verify that adjacent construction is suitable for installation of door.

- Verify that electrical utilities have been installed and are accessible.

- Verify clear opening dimensions and that door opening is plumb.

- Notify Architect/ General Contractor of any unacceptable conditions or varying dimensions.

#### INSTALLATION

  - Install in accordance with manufacturer’s instructions, shop drawings and NFPA 80.

  - Install doors plumb and parallel with the finished floor.

  - Installation shall be performed by factory trained and certified installers with experience installing electrically operated, accordion-folding doors.

#### 3.03	ADJUSTMENT

- Adjust door installation to provide uniform clearances and smooth, quiet, non-binding operation.

- Test that all operations are functional and meet the requirements of local codes.

#### 3.04	CLEANING

- A.	Clean surfaces using manufacturer’s recommended means and methods.

#### 3.05	INSTRUCTION

    - Following the installation and final adjustments, the installer shall fully instruct the General Contractor as to the correct operating procedure and safety requirements of the door package.

#### 3.06	STORAGE OF WASTE AND RECYCLING

- Store and recycle waste in accordance with Section 01 74 19 Construction Waste Management and Disposal.

- 3.07	MAINTENANCE

- A.   Engage a Door Systems, authorized service representative, Doorsysinc.com 714-258-7100, to test, adjust, and maintain the system once per annum as required per NFPA 101 and NFPA 80.

END OF SECTION