#### SECTION 08 35 13.23 – WON-DOOR FIREGUARD ACCORDION-FOLDING FIRE DOORS     (+ OPTIONAL ACCESS CONTROL)

#### PART 1 – GENERAL

#### SUMMARY OF WORK

- Division 0 and 1, as indexed, apply to this section.

- Furnish and install all horizontal-sliding accordion-folding fire doors shown on the drawings and specified herein.

#### 1.02	RELATED SECTIONS

- All headers, support structures, fire protection of support structures, surrounding insulation, jambs, storage pockets, blocking and trim shall be furnished and installed by other sections.

All electrical wire, wiring, conduit and electrical boxes shall be furnished and installed by electrical section including connections to smoke detectors and building fire and access control alarm panels.

Drilling/placement of anchorage points into pre or post tensioned decks, welding/ punching/drilling steel members and all drywall work by other sections.

OPTION: All track, soffit, chain guide and striker shall be painted by Section 09 90 00. Color shall be selected by the architect.

OPTION: If Section 2.05 B, Individual LCD Door Status Display is selected as an option, the following paragraph should be included:  Wiring for Individual LCD Door Status Display at fire door-One (1) modular telephonic connector, 6 position 4 or 6 contact (USOC RJ14-6P4C or -6P6C) jack shall be supplied at the back of the storage pocket and tied to the 4 square junction box adjacent to the door with CAT 5 cable.  The junction box, modular jack and wire shall be furnished and installed by the electrical section.  Termination to the LCD panel shall be by punch down block (IDC) and shall be by the electrical section as per the manufacturer’s instructions.

OPTION: If Section 2.05 E, Remote Access Control is selected as an option, the following paragraph should be included: Interface to the doors is to be accomplished by use of a LOK Module and a remote line interface.  A twisted pair of stranded 18-gauge copper conductors is to be provided between the LOK Module at the door location and the remote line interface (5,000’ max. wire length).  Wiring from the remote line interface (RLI) to the control device shall be stranded 18-gauge copper conductors (20’ max. distance from control device).

OPTION: If Section 2.05 F, Remote Monitoring is selected, the following paragraph should be included: Form C dry contact relays for supervisory, trouble, door status, and alarm condition located in the Won-Door controller, shall provide output signals for monitoring the door condition. For 2 additional output signal requirements, an XRM (Auxiliary Relay Module) will be included.  A twisted pair of stranded 18-gauge copper conductors for each output is required from the Won-Door controller to the monitoring device location.

#### 1.03	QUALITY ASSURANCE

- Installation shall be performed by factory trained and certified installers with experience installing electrically operated accordion folding fire doors.

- Doorsysinc.com 714-258-7100

Fire doors shall be listed by Underwriters Laboratories for ratings as indicated, when tested in accordance with the requirements of UL 10B and NFPA 252.

Automatic closing system shall be listed by Underwriters Laboratories in accordance with the requirements of UL 864 and UL 294, and in compliance with NFPA 80.

Fire doors used for smoke and draft control shall bear the “S” mark on the fire door UL label and shall have an air leakage of less than 3 CFM/ft2 at 0.1 inch of water column pressure when tested in accordance with UL 1784 with an artificial bottom seal.

Fire doors used at the point of access to an elevator or elevator lobbies used by fire service personnel for evacuations shall bear the “S” mark on the UL fire door label and shall have an air leakage of less than 3 CFM/ft2 at 0.1 inch of water column pressure when tested in accordance with UL 1784 without an artificial bottom seal.

Fire Doors shall be capable of resisting an air pressure differential up to 0.05 inches of water column.  Optional air pressure resistance up to 0.15 inches of water column available. (See 2.05 H)

#### 1.04	SUBMITTALS

- See Section 01 30 00 – Administrative Requirements, for submittal procedures.

Product Data: Provide manufacturer’s technical literature, include UL listing data.

Shop Drawings:  Indicate construction and installation details and dimensions, including layout, electrical requirements, required stack depth, height of header above finished floor, and requirements for anchorage and support of each door.

Operation and Maintenance Data:  Operating procedures, troubleshooting and repair methods, and wiring diagrams.

#### 1.05	DELIVERY, STORAGE, AND HANDLING

- Door Systems will deliver original, unopened packages to a location designated by the General Contractor.  All packages must be stored indoors, protected from moisture damage and secure from theft or other damage.  General Contractor to note any damage or shortages at time of delivery.

#### 1.06	COORDINATION BY GENERAL CONTRACTOR

- Coordinate with the following:

  - Fire Alarm system.

  - Electrical.

  - Pocket cover doors (if required).

  - Floor and ceiling finish.

- Assure accurate installation of header, jamb, and trim.  Provide “As-Built” dimensions for opening and storage pocket.  Supervise unloading and handling of materials.

- Store boxes flat (not more than three high) in a protected dry area.

Permanent power shall be in-place and ready for final connection when fire and access control doors are installed. Assure access to and proper clearance for motor operators.

After testing the fire alarm system, automatic-closing fire doors shall be re-set to the original position.

- 1.07	WARRANTY

- Materials and installation shall be warranted against defects in workmanship for a period of two (2) years from the date of substantial completion.

#### PART 2 – PRODUCTS

#### 2.01	MANUFACTURERS

- Horizontal-sliding, accordion-folding, fire doors as manufactured by Won-Door Corporation and supplied and installed by Doorsysinc.com 714-258-7100 shall be specified as the following:

- Won-Door FireGuard ____ (select one: 20, 60, 90, 120, 180; S, E, TR – number designates minutes of fire rating, E for point of access to an elevator). (Note: “TR” for temperature rise of not more than 450 F above ambient at 30 minutes. (When specifying “TR” doors, contact the manufacturer for pocket depths, hanging weight and size limitations.)

No substitutions allowed.

#### 2.02	ACCORDION FIRE DOORS – GENERAL

- Provide electrically powered self-closing fire doors of configurations indicated on the drawings.

  - Fire rating as required.

Fire Rating – Fire doors shall be listed by Underwriters Laboratory as special purpose fire doors having a (select one: 20, 60, 90, 120, 180) minute fire protection rating in accordance with the requirements of UL 10B and NFPA 252.

Single Parting and Bi-Parting: Door opening can be configured in a single parting (pocket at one end) or bi-parting (pocket at both ends) condition.

Closing and Opening Operation:  Automatic Closing System, listed to UL864 including motor operator and releasing devices shall be a Microprocessor-based system and shall commence closing upon activation by fire signal, access control signal, low battery voltage or optional low AC voltage.

  - Obstruction Detection:  Contact with an obstruction shall cause the door to stop, reverse enough to remove pressure on the leading edge, pause, and then re-close when in an alarm condition.

  - Constant pressure to the leading edge while not under motor power shall prevent motor operation and allow the door to be opened manually.

Exit Device Operation: Provide an exit device on one or both sides of door.

  - In emergency mode, a slight pressure on the exit device will cause the door to open a minimum of 32 inches, pause for 3 seconds, and then automatically close.

  - The open distance shall be field programmable, up to the entire opening width.

  - The pause before re-close shall be field programmable up to 30 seconds.

  - The exit device shall have the ability when not in the emergency (fire) mode to be used to open the door and move it back into the storage pocket.

- 2.03	ACCORDION FOLDING FIRE DOORS + ACCESS CONTROL – GENERAL

- FireGuard + Access control doors restrict access and protect occupants against forced entry in designated areas of the building.  They are equipped with the following features:

  - Two parallel accordion type walls independently suspended for advanced security protection (Single wall systems not permitted).

  - Anti-Sway brackets (resists 50 lbs. of lateral force with less than 6” of lateral movement with no floor track or other devices securing the door to the floor).

  - Lock (motor brake secures the door in position with up to 600 lbs. resistance).

  - Heavy duty track support system (counters excessive use and abuse conditions).

  - Security jamb stops (secures the jamb end of the door in the pocket).

  - Reset device: A reset device is required to clear the door from alarm and fault mode   (See 2.05 G for reset device options).

Options:

- High speed motor (operates the door at 18” per second).

- Remote Control (LOK Module and RLI interconnect boards provide a remote line interface for simple integration to the building security system.  Remote line interface allows a maximum distance of 5,000’ from security system to FireGuard location.  See 2.05 E for full description of capabilities).

- Remote Monitoring: Form C dry contact relays for supervisory, trouble, door status, and alarm condition located in the Won-Door controller, shall provide output signals for monitoring the door condition.  A twisted pair of stranded 18-gauge copper conductors for each output is required from the Won-Door controller to the monitoring device location. (See 2.05 F for full description of capabilities).

- Door Operation:  Automatic Closing System, listed to UL864 and UL294 including motor operator and releasing devices shall be a Microprocessor-based system and shall commence closing upon activation by access control signal from security controller.

            - Obstruction Detection:  Contact with an obstruction shall cause the door to stop, reverse enough to remove pressure on the leading edge, pause, and then re-close when in an alarm condition.

- Exit Device Operation: Provide an exit device on one or both sides of door.

  - In security mode, a slight pressure on the exit device on the egress side of the door will cause the door to open to a designated pre-set distance, pause for 3 seconds, and then automatically close.  The exit device on the ingress side (secured side) of the door may be excluded.  If it is included, it will be disabled to prevent unauthorized access.  An owner selected control device will allow credentialed individuals access through the secured side.

  - The open distance shall be field programmable, up to the entire opening width.

  - The pause before re-close shall be field programmable up to 30 seconds.

  - The exit device shall have the ability when not in security mode to be used to open the door and move it back into the storage pocket.  When fire mode occurs, the exit device(s) will be fully activated.

#### 2.04	COMPONENTS

- Door Construction: Two parallel, accordion-type walls independently suspended with no floor tracks or pantographs.

  - Panels: 24-gauge steel, V-grooved; modular in design; capable of in-place repair.

  - Perimeter Seals: shall consist of continuous extruded sweeps attached to the top and         bottom of the fire door to form a smoke and draft seal.

  - Hanging Weight: 5.5 pounds per sq. ft when extended across opening.

  - Finish:  All steel panels shall have factory-applied protective coatings.

  - Color:  Manufacturer’s standard platinum.

- Suspension System: Two tracks, on 8- or 10-inch centers, attached to overhead structural support.

  - Track: 14-gauge cold rolled steel or 1/8” Aluminum extrusion.

  - Panel Hangers:  Panels shall be suspended by a steel hanger pin and ball bearing roller system.

  - Narrow Lead Post Hangers: 8-wheel ball bearing trolley.

  - Flat Lead Post Hangers: Double ball bearing rollers at each side with an 8-wheel ball bearing trolley.

- Power source shall be: 120-volt AC input.  System operation voltage shall be dual sourced from DC power supply and backup battery.

- Automatic Closing System shall be listed to UL864 including capability to send and receive signals from the Fire Control Panel and shall consist of the following:

  - Microprocessor based Electronic Control box with the ability to:

    - Monitor dual power sources continually for peak performance including:

      - Detect a missing battery, bad battery, or low battery condition.

      - Detect if the charging circuit is bad.

      - Detect fuse failures.

      - Detect high or low AC conditions.

    - Monitor the health of the drive train.

    - Monitor inputs including faults associated with door block, exit device, patron hardware, and key switches.

    - Run a “watch dog” monitoring circuit which will force a software restart in the event the software hangs, including tracking the number of resets that occur for diagnostic purposes.

    - Withstand aberrant voltages up to 120 volts AC on the fire alarm input circuit without damage including the ability to indicate that the alarm circuit has not been wired as a dry contact, “no voltage” circuit when errant voltages are applied to the circuit.

    - Communicate with other microprocessors on the system via an internal bus system.

    - Indicate faults or supervised information both locally and at a remote location.

  - Motor Operator Assembly including a DC gear-motor, drive sprocket, clutch, and position sensors.  The motor shall drive the door by means of a chain.  Standard motor drive speeds range from 6”-10” per second.

    - High speed motor operation up to 18” per second is available for conditions requiring high occupant load egress and limited access control.

    - Leading Edge shall be pressure sensitive such that contact with an obstruction shall cause the door to stop, pause for a minimum of 3 seconds, then re-close when in alarm mode.

  - Exit Device will be located on each side of the door. (Standard operation when access control is not included).

  - An optional key switch by others may be provided for operating the door opened and closed when not in fire mode.  Location of the key switch to be provided by the architect.

- The header shall be provided as an integrated part of the door assembly and shall Include track, threaded rods and mechanical attachment hardware.

  - OPTIONS

- Vision Panel consisting of a frame and clear glass assembly listed by Underwriters Laboratory (Note: Required on cross corridor applications in healthcare facilities).

- Individual LCD Door Status Display Panel shall be provided adjacent to the door to indicate in the English language the status of the door, i.e., door position and trouble conditions.  It shall have a port that allows easy access to a diagnostic tool for the purposes of field programming the door to customized settings.

- Backlit Exit Device. High intensity LED illuminated exit device increases visibility and provides a more effective identification of exit location.

- Wireless Exit Device may be used when an exit device is desired on an adjacent wall to the door opening and providing wiring is not a possibility.  Using energy harvesting technology (no batteries required), exit device can be installed in close location.  Kit consists of activation button, wireless transmitter and wireless access module.  Can be mounted directly to the wall.

- Remote Access Control.  A locking interface to the access control doors shall be accomplished using a Won-Door Corporation supplied LOK Module and RLI (Remote Line Interface).  Said modules shall be capable of remote inputs for Lock/Unlock, Panic Lock, Key Close, Key Open, Patron Devices (PAT), Tamper, and Tamper Clear. The RLI shall be located within 20 wire feet of the owner provided security controller. The LOK Module is located at the back wall of each FireGuard storage pocket.  Maximum distance between the RLI and the LOK Module shall be 5,000 feet.  The lines between the LOK module and the RLI shall be fully supervised for line shorts, open lines, and lines shorted to ground.  The RLI inputs can activate with dry contacts, or they can be driven by voltages between 12-24 DC volts.  Each circuit has a separate selector switch for the dry contact vs voltage style inputs.

- These inputs shall be dry, no voltage contacts as follows:

  - LOCK/UNLOCK – When the circuit is open the door shall be open and unlocked.  When the circuit is closed the door shall be closed and locked.  Locked shall mean that only credentialed inputs will open the door.  The open circuit – open door, closed circuit – locked door shall be capable of being switched to open circuit – locked door, closed circuit – open door via a hardware jumper.

  - PANIC LOCK – When this circuit labeled “PANIC” is held closed, the door shall lock and shall ignore the patron input from the LOK Module until this circuit is restored to normal operation.  While the circuit is in the panic state credentialed inputs from other sources besides the LOK module shall be accepted.  This input shall be capable of activating on an open circuit instead of a closed circuit by installing a jumper across the NC jumper contacts.  Once the circuit is restored to normal operation, the first activation of the LOK module patron input (PAT) or any other PAT input shall reset the door out of PANIC and cause the door to open.

  - Key Close – When this circuit closes it shall cause an open door to start closing, an opening door to stop, and if held for 3 seconds the door to reset from fire or panic incidents if the underlying inputs (Fire and/or panic) have been previously released.

  - Key Open – When this circuit closes it shall cause a closed door to start opening and a closing door to stop.

  - PAT (Patron Device) – When this circuit is closed it shall cause the locked door to open to a field programmable distance.  It shall hold at that location until the circuit opens after which it shall delay a field programmable duration from 3 to 30 seconds and then cause the door to reclose.  If the door is closed but not locked it shall open to the programmed distance but not reclose.

  - TAMPER – This circuit shall be a normally closed circuit that when opened causes the TAMPER FAULT to occur as described in the UL 294 Access Control Standard.

  - CLEAR – This circuit when held closed for five seconds shall clear the tamper alarm provided it is being asserted at least 2 minutes after the TAMPER circuit has been restored to normal operation.

- Remote monitoring.  The doors shall be monitored by providing one pair of 18-gauge wires from the monitoring station to each Won-Door location for each condition to be monitored.  Normally open dry contact relays for supervisory, trouble, door status, and alarm conditions are provided in the Won-Door controller. If additional outputs are required to monitor the doors, an additional auxiliary relay module (XRM) shall be provided with two additional relays to indicate specific status and fault conditions including any two of the following:  Open, Opening, Closing, Stopped, Locked, Exit Device Access, Secure Access, Forced Entry, TLS Failure, Key Switch Failures, Stuck switches, Power Failures, Communication Errors.

- Reset Devices (required to clear the door from fault and alarm mode.)  Options include:

  - Key Switch by others (Requires a 2 position, spring activation to neutral, normally open switch).

  - Key switch by Won-Door.

  - Wireless Key Switch by Won-Door using energy harvesting technology (no batteries required) for same room installation consisting of a key cylinder and wireless transmitter in an [ON/OFF/ON] configuration and wireless access module.

  - Wireless Reset Device by Won-Door using energy harvesting technology (no batteries required) for same room installation consisting of a wall mounted device that accepts any key card to activate a wireless transmitter that can be mounted directly to the wall. Requires Wireless Access Module to operate.

- Air Pressure Resistance.  When an air pressure differential is present at the door location, the standard door shall be capable of resisting an air pressure differential of 0.05” of water column.  For air pressure differentials of 0.05” to 0.1” w.c., anti-sway brackets shall be placed interior to the door approximately every five (5) feet or less and lead post outriggers shall be provided.  For air pressure differentials of 0.1” to 0.15” w.c., a reinforced vertical bar shall be provided at the lead post and a self-leveling lead post assembly shall provide motorized tracking of the leading edge of the door to assure proper closure at the striker.

- Obstruction Test will enable all doors to be checked for obstructions every 24 hours.  When enabled, the door will close across the opening to assure there has been no obstructions placed in the door path.  If no obstruction is encountered, the door returns to the pocket location.  If an obstruction does occur, the door will stop at the location of the obstruction and sound an alarm.  Once the obstruction is removed, the alarm can be cleared and the door returned to the pocket location.

- Infrared Obstruction Detector is an infrared light beam provided to monitor the opening path.  If an object is placed in the path of the door for more than 3 minutes, the beam shall cause the door to sound an alarm indicating a path obstruction.

#### RELATED CONSTRUCTION

- Track Support Construction:  Provide supports attached to structure and mounting surface for track including drilling/placement of anchorage points into pre or post tensioned decks, welding/punching/drilling steel members, and all drywall work; comply with door manufacturer’s instructions and recommendations.

- Pocket Construction:  Provide rated pocket as specified for storage of accordion door when open; comply with door manufacturer’s instructions and recommendations.

- Protection: Protect installed work from damage.

#### PART 3 – EXECUTION

#### 3.01	EXAMINATION

- Verify that adjacent construction is suitable for installation of door.

- Verify that electrical utilities have been installed and are accessible.

- Verify clear opening dimensions and that door opening is plumb.

- Notify Architect of any unacceptable conditions or varying dimensions.

#### 3.02	INSTALLATION

- Install in accordance with manufacturer’s instructions, shop drawings and NFPA 80.

- Install fire doors plumb and parallel with the finished floor.

- Installation shall be performed by factory trained and certified installers with experience installing electrically operated accordion folding fire doors.

#### 3.03	ADJUSTING

- Adjust door installation to provide uniform clearances and smooth, quiet, non-binding operation.

- Test that all operations are functional and meet the requirements of local codes.

#### 3.04	CLEANING

- Clean surfaces using manufacturer’s recommended means and methods.

#### 3.05	STORAGE OF WASTE AND RECYCLING

- Store and recycle waste in accordance with Section 01 74 19 Construction Waste Management and Disposal.

- 3.06	MAINTENANCE

- A. Engage a Door Systems, authorized service representative, Doorsysinc.com 714-258-7100, to test, adjust and maintain the system once per annum as required per NFPA and NFPA 80.

END OF SECTION 08 35 13.23